PART 1 GENERAL

1.01	SUMMARY

A.	Section Includes: This Section specifies design, supply and installation of window washing systems and suspended maintenance equipment.

1.02	RELATED SECTIONS

A.	Section [01 31 19 – Project Meetings]

B.	Section [01 61 00 – Common Product Requirements]

C.	Section [01 74 00 – Cleaning and Waste Management]

D.	Section [03 30 00 - Cast-in-Place Concrete: concrete runway, piers and sleepers for roof cars].

E.	Section [05 05 23 - Metal Fastenings: horizontal lifeline fasteners].

F.	Section [05 50 00 - Metal Fabrications: monorail and davit system cantilevered support brackets].

G.	Section [07 62 00 - Sheet Metal Flashing and Trim: aluminum flashing for davit bases].

H.	Section [08 44 00 - Curtain Wall and Glazed Assemblies: mullion and stabilization co-ordination].

I.	Section [26 00 00 - Electrical: climbing monorail power supply].

J.	Section [26 25 00 - Enclosed Bus Assemblies: climbing monorail busbar].

K.	Section [01 78 00 - Closeout Submittals].

1.03	REFERENCES

A.	American Institute of Steel Construction (AISC).

1.	AISC S342L [1993], Load and Resistance Factor Design Specification for Structural Steel Buildings (including Supplement No.1).

B.	Aluminum Association (AA).

1.	AA DAF 45, Designation System for Aluminum Finishes.

2.	AA ADM-1 [2000], Aluminum Design Manual.

D.	American Society of Mechanical Engineers (AMSE).

1.	ASME A120.1 [2006], Safety Requirements for Powered Platforms and Traveling Ladders and Gantries for Building Maintenance.

E.	American National Standards Institute / International Window Cleaning Association (ANSI/IWCA).

1.	ANSI/IWCA I-14.1 [2006], Window Cleaning Safety Standard.

F.	American Welding Society (AWS).

1.	AWS D1.2/D1.2M [2003], Structural Welding Code - Aluminum.

2.	AWS D1.1/D1.1M [2006], Structural Welding Code—Steel.

G.	ASTM International (ASTM).

1.	ASTM A123/A123M [2002], Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

2.	ASTM A167 [1999 (2004)], Specification for Stainless and Heat Resisting Chromium Nickel Steel Plate, Sheet and Strip.

3.	ASTM A276 [2006], Standard Specification for Stainless Steel Bars and Shapes.

4.	ASTM A492 [1995 (2004)] Standard Specification for Stainless Steel Rope.

5.	ASTM B221 [2006], Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

H.	International Code Council (ICC).

1.	International Building Code.

I.	Occupational Safety and Health Administration (OSHA).

1.	OSHA 1910, Subpart D, Walking and Work Surfaces.

2.	OSHA 1910, Subpart F, Appendix C, Personal Fall Arrest Systems.

3.	OSHA Ruling on Window Cleaning by Bosun’s Chair.

4.	OSHA 1910.66 Subpart F, Powered Platforms.

J.	National Roofing Contractor’s Association (NRCA)

1.	The NRCA Roofing and Waterproofing Manual, Fifth Edition.

K.	Uniform Building Code (UBC).

1.04	ACTION SUBMITTALS

A.	General: Submit listed action submittals in accordance with Contract Conditions and Section [01 33 00 - Submittal Procedures].

B.	Shop Drawings: Indicate information on shop drawings as follows:

1.	Submit shop drawings showing complete layout and configuration of window cleaning and suspended maintenance system, including components and accessories.

2.	Indicate design and fabrication details, window "drops", hardware, and installation details.

3.	Include installation and rigging instructions and:

a.	Required restrictive working usage and general safety notes.

b.	Non-restrictive working usage and general safety notes.

4.	Ensure Shop Drawings are reviewed by Engineer licensed in State of Maryland and submit calculations to Architect, Consultant and/or Owner.

C.	Submit product data, including manufacturer’s technical data sheet, for specified products.

1.05	INFORMATION SUBMITTALS

A.	Quality Assurance:

1.	Test Reports: Certified test reports showing compliance with specified performance characteristics and physical properties.

2.	Certificates: Product certificates signed by manufacturer certifying materials comply with specified performance characteristics and criteria and physical requirements.

3.	Manufacturer’s installation instructions.

C.	Manufacturer’s field reports specified.

1.06	CLOSEOUT SUBMITTALS

A.	Submit 1-year standard manufacturer warranty documents specified.

B.	Operation and Maintenance Data: Submit Operation and Maintenance data for installed products in accordance with Section [01 78 00 - Closeout Submittals].

1.	Include:

a.	Manufacturer’s instructions covering maintenance requirements and parts catalog giving complete list of repair and replacement parts with cuts and identifying numbers.

b.	[1] copy of system Equipment Manual & Inspection Log Book, with "Initial Inspection - Certification for Use" and "Inspection Sign-Off" forms completed.

c.	[2] copies of reduced, “as-built shop drawing” showing equipment locations and details. Ensure drawing is posted adjacent exits to roof.

1.07	QUALITY ASSURANCE

A.	Qualifications:

1.	Installer experienced in performing work of this section who has specialized in installation of work similar to that required for this project.

2.	Manufacturer Qualifications: Manufacturer capable of providing field service representation during construction and approving application method.

B.	Regulatory Requirements.

1.	Comply with [Uniform Building Code (UBC)] [International Building Code (IBC)] [Building Code for State of Maryland.

2.	Comply with OSHA regulations as follows:

a.	1910, Subpart D, Walking and Working Surfaces.

b.	Appendix C to 1910 Subpart F, Personal Fall Arrest Systems.

c.	OSHA Ruling on Window Cleaning by Bosun's Chair.

d.	1910.66, Subpart F, Powered Platforms.

1.08	DELIVERY, STORAGE AND HANDLING

A.	General: Comply with [01 61 00 - Common Product Requirements].

B.	Ordering: Comply with manufacturer’s ordering instructions and lead time requirements to avoid construction delays.

C.	Delivery:

1.	Deliver materials in manufacturer’s original packaging with identification labels intact and in sizes to suit project.

D.	Storage and Protection:

1.	Store materials protected from exposure to harmful weather conditions and at temperature conditions recommended by manufacturer.

E.	Transportation and Handling:

1.	Ensure center of gravity of davits weighing [80] lbs ([36.3] kg) or greater remains [36] inches ([915] mm) maximum above safe surface while transporting.

2.	Ensure davits requiring [80] lbs ([36.3] kg) or greater lifting effort are equipped with are equipped with mechanical means of hoisting into position.

1.09	PROJECT AMBIENT CONDITIONS

A.	Installation Location: Assemble and erect components only when temperatures are above [40] degrees F ([4] degrees C).

1.10	SEQUENCING

A.	Sequence with other Work and Comply with window washing equipment manufacturer’s written recommendations for sequencing construction operations.

1.11	WARRANTY

A.	Project Warranty: Refer to Contract Conditions for additional project warranty provisions.

B.	Manufacturer’s Warranty: Submit, for Owner’s acceptance, manufacturer’s standard warranty document executed by authorized company official. Manufacturer’s warranty is in addition to, and does not limit, other rights Owner may have under Contract Documents.

C.	Warranty: Commencing on date of substantial completion set by Owner, Architect and/or Consultant.

PART 2 PRODUCTS

2.01	MANUFACTURERS

A.	Ensure manufacturer has minimum [5] years experience in manufacturing window washing and suspended maintenance system components similar to or exceeding requirements of project.

B.	Manufacturer’s Insurance: Ensure manufacturer carries liability insurance to protect against product and system failure in amount of [five million dollars US ($5,000,000)] minimum.

2.02	PROPRIETARY PRODUCTS AND SYSTEMS

A.	Manufacturer: Pro-Bel Group of Companies, Phone: (905) 427-0616, USA Toll Free: (800) 461-0575, Fax: (905) 427-2545, E-mail: info@pro-belgroup.com, Internet URL: www.pro-bel.com

2.03	DESIGN PERFORMANCE REQUIREMENTS

A.	Design window cleaning and suspended maintenance system to suit project requirements to [AISC S342L] [and as indicated].

B.	Locate anchorages to suit suspension equipment specified.

C.	Design anchor components for cleaning and suspended maintenance equipment to [ASME A120.1].

1.	Ensure compatibility with industry standard equipment.

2.	Anchorage and anchor components: Designed by Engineer qualified in design of window cleaning and suspended maintenance equipment and licensed in State of Maryland.

D.	Design system fall arrest safety anchors and equipment supports to [AISC S342L (including supplement No.1)] [and ANSI/IWCA I-14.1], and as follows:

1.	Comply with OSHA 1910, Subpart F, Appendix C.

2.	Supports for Suspended Platforms including davits, rigging sleeves and monorail:

a.	Safety factor against fracture or detachment: 4 to 1.

a.	Vertical service load: [1000] lbs ([4.45] kN) minimum.

b.	Rated load against fracture: [4000] lbs ([17.8] kN) minimum.

3.	Fall Arrest Safety Anchors:

a.	Fall arresting force safety factor of 2 to 1 without permanent deformation: [1800] lbs ([8.0] kN) minimum.

b.	Fall arrest force against fracture or detachment: 5,000 lbs (22.4kN) minimum.

E.	Trolley Systems: Design, fabricate and finish trolleys to ensure no structural or mechanical deterioration over designed life that could affect security and operation considering permanent exposure to elements.

1.	Provide rotating components with sealed-for-life rolling element bearings protected from environment.

2.04	EQUIPMENT

A.	Davits.

B.	Permanent Powered Platform

2.06	DAVITS

A.	Davit Booms: Roof rigged, aluminum sections of engineered length and size to suit application, equipped with: carrying handles; stainless steel rolling trolley [on outboard end, designed to carry 1000 lbs (4.5 kN) vertical service load, minimum.

1.	Ensure non-corrosive UV resistant data plate stating Maximum Service Capacity of boom, Manufacturer's Name, Serial No., Manufacturing Date, rated load and other pertinent information is prominently displayed.

B.	Davit Masts: Round tubular [aluminum][steel] section capable of rotating through 360° with carrying handles and connecting pins.

C.	Davit Arms: Davits to be demountable, portable, capable of being easily and quickly broken down into pieces weighing 140 lbs (73 kg) maximum.

1.	Ensure davit arm booms equipped with rolling trolleys or friction trolleys have stops to prevent detachment from boom.

- Provide hoisting winches and dolly wheels.

D.	Davit Bases: Round, mild steel, hollow section piers, Type 350W with [50] Ksi ([350] MPa) minimum yield strength, [hot dipped galvanized to ASTM A123/A123M] [manufacturer’s polyurethane/polyurea coating system] [with [0.75] inches ([19] mm) diameter U-bar safety anchor, and securement to suit application.

E.	Acceptable Material: Pro-Bel Group, Davit System

2.11	PERMANENT POWERED PLATFORMS

A.	Suspended Platform: Type 6061-T6 aluminum alloy to ASTM B221, mill and powder coated finished modular platform system to ASME A120.1, engineered length and width [to suit application] [as indicated] and based on load bearing frame, with non-slip, aluminum deck, soft rubber wall rollers and caster wheels.

1.	Provide integral, detachable [36] inches ([915] mm) long single work cage at one end complete with necessary components to meet project requirements.

2.	Comply with OSHA 1910.66 Subpart F, Powered Platforms.

B.	Frame and Rails:

1.	Side frames and connecting frames: [Structural aluminum] [Galvanized mild steel] [Powder coated steel].

2.	Guard rails and guard rails posts: Square, thick wall aluminum extrusions with rails [36] inches ([915] mm) minimum, above deck level at working side of platform, [42] inches ([1067] mm) at non-working side.

3.	Include [3.5] inches ([90] mm) high toe-board around circumference of platform with spaces between toe-board and top guardrails covered with expanded aluminum screen.

a.	Leave space between intermediate guardrail and top guardrail open without aluminum screen at front side of platform.

C.	Stirrups: [Structural aluminum] [Galvanized mild steel] [Powder coated steel] fitted with manufacturer's standard hoist unit, top limit switch assembly, striker plate, and high "fair lead".

1.	Wire winders: [Electric powered] [Passive type] with [single] [twin] drum built into stirrups.

a.	Capacity: [______], [to suit project requirements] [as indicated].

b.	Dimensions: [______], [to suit project requirements] [as indicated].

D.	Cable Storage Bin: Include cable storage bin on rear guard rail.

1.	Capacity: [______], [to suit project requirements] [as indicated].

2.	Dimensions: [______], [to suit project requirements] [as indicated].

E.	Safety Controls:

1.	Electro mechanical overload system: Integral with each hoist preset to safe working load plus 25% minimum, and designed to operate limit switch and cut power supply if platform overloads.

2.	Include upper limit switch assembly at each stirrup top and ensure system cuts electric power supply when switch contacts striker plate on suspension rope at top limit of travel.

3.	Lower limit trip bar assembly: Hinged aluminum bar at each end of platform working face underside.

a.	Design to ensure limit switch interrupt electric power supply to both hoists if bar is pushed upwards by obstruction on building facade during descent. Ensure system continues to allow platform to operate in upward direction.

F.	Main and Auxiliary Control Boxes: Include electric control gear for both hoists and wire winder motors contained in central control box and mounted on rear guardrail. Include components as follows:

1.	Switches marked “UP/DOWN” and "HOLD TO RUN".

2.	Hoist selector switch marked “LEFT/RIGHT/BOTH”.

3.	Bottom trip bar over-ride button.

4.	Emergency stop button.

5.	Platform self-leveling system.

6.	Power “ON” indicator light.

7.	Three phase protection and light indicator.

8.	Locking facility on main switch.

9.	Hand wheel for manual hoist operation.

10.	Watertight electrical "quick" connections.

11.	[______]

G.	Hoist Unit: Power platform using 2 UL listed traction type hoists with features as follows:

1.	30 amp 230 volt 60 Hertz hoist with lift capacity to suit platform weight and live load.

2.	[35] feet per minute ([10.7] metres per minute) minimum speed.

3.	Slack rope safety device acting on safety rope.

4.	Electro mechanical overload system.

5.	Electro mechanical main brake.

6.	"No Power" controlled emergency descent system.

7.	Hoist protection cover.

8.	Main line power protection: [HBL2720SW, NEMA No.15-30R] [HBL2620SW, NEMA No. L6-30R].

a.	Acceptable material: Hubbell Twist-Lock 230 volts, 3 phase, 60 Hertz, 30 amps receptacle .

9.	[______].

H.	Steel Wire Rope: Ensure platform is complete with [2] [4], 6 x 19 Seale and IWRC, [0.3125] inches ([8] mm) minimum diameter galvanized high tensile steel wire ropes, length to suit project requirements.

1.	Ensure each rope include [3] lbs ([1.4] kg) minimum safety hook with thimble talurit clamp and brazed "bullet-end".

I.	Electrical Supply Cable: Fit trailing supply cable with cable support clamp and CEE plug for connection to central control box. and supplied with cable support clamp.

1.	Electrical supply cables: [100] [400] feet ([30] [120] m) long with reinforced core.

J.	Powered Platform Accessories:

1.	Portable fire extinguisher securely attached to platform.

2.	Water container attached to rear guard rail.

3.	Electric power tool receptacle on central control box.

K.	Powered Platform Stabilization (Tie-In Guides):

1.	Continuous stabilization: Provide guide roller/sliding shoe assembly at each end of bottom of platform designed to provide continuous engagement between platform and internal tracks.

a.	Co-ordinate design with [curtain wall manufacturer] [Section 08 44 00 -Curtain Wall and Glazed Assemblies] to ensure smooth operation.

b.	Internal track tie-in guides: Opening [1] inch ([25] mm) minimum with [2.5 x 2.5] inches ([64 x 64] mm) minimum inside dimensions. Design tracks to ensure platform trolleys can be inserted from top and bottom of building.

2.	Intermittent stabilization anchor buttons: Buttons:[Stainless steel] [1.5] inches diameter x [0.1875] inches ([38] mm diameter X [5] mm) thick with Allen head recess, with threaded [stainless steel] building anchor insert of size and configuration to suit building facade. Include sufficient quantity of [stainless steel] stabilizer ties.

a.	Working load: To AISC S342L, [300] lbs ([1.33] kN) minimum.

b.	Load against fracture or detachment: To AISC S342L, [600] lbs ([2.67] kN) minimum.

c.	Locate buttons [every third floor] [ [40] [50] feet ([12.2] [15.3] m) maximum] in line with davit base suspension points.

d.	Acceptable material: Pro-Bel Group, Stainless Steel Stabilization Buttons.

3.	Detent pins: [Stainless steel], [0.3125] [0.375] inches ([8] [10] mm) diameter tie handles with spring loaded ball lock to suit building facade. Include sufficient quantity of [stainless steel] stabilizer ties.

a.	Working load: To AISC S342L, [300] lbs ([1.33] kN) minimum.

b.	Load against fracture or detachment: To AISC S342L, [600] lbs ([2.67] kN) minimum.

c.	Locate detent pins [every third floor] [ [40] [50] feet ([12.2] [15.3] m) maximum] in line with davit base suspension points.

d.	Acceptable material: Pro-Bel Group, Stainless Steel Detent Pins.

L.	Acceptable Material: Pro-Bel Group, Permanent Powered Platform.

2.20	ELECTRICAL REQUIREMENTS

B.	Ensure main line power is located [100] feet ([30] m) maximum from powered window washing equipment.

C.	Ensure power outlets experience 3% maximum voltage drop under full load.

2.22	SOURCE QUALITY CONTROL

A.	Ensure window washing equipment components and materials are from single manufacturer.

2.23	PRODUCT SUBSTITUTIONS

A.	Substitutions: [In accordance with Section 01 25 13 - Product Substitution Procedures [No substitutions permitted].

PART 3 EXECUTION

3.01	INSTALLERS

A.	Provide experienced and qualified technicians to carry out erection, assembly and installation of window washing and suspended maintenance equipment system.

B.	Do steel welding to AWS D1.2/D1.2M.

C.	Do aluminum welding to AWS D1.1/D1.1M.

3.02	MANUFACTURERS INSTRUCTIONS

A.	Compliance: Comply with manufacturer’s written data, including product technical bulletins, product catalog installation instructions and Pro-Bel Group technical data sheets.

3.03	EXAMINATION

A.	Site Verification of Conditions:

1.	Verify that substrate conditions which have been previously installed under other sections or contracts, are acceptable for product installation in accordance with manufacturer’s instructions prior to installation of window washing equipment.

2.	Inform [Owner] [Architect] [Consultant] of unacceptable conditions immediately upon discovery.

3.	Proceed with installation only after unacceptable conditions have been remedied.

3.04	PREPARATION

A.	Ensure structure or substrate is adequate to support complete window washing equipment system.

B.	Ensure structural steel to receive safety anchors [has adequate bearing surface as indicated on shop drawings] [and] [has 100% welds between anchors and structural steel].

3.05	INSTALLATION

A.	Coordinate window washing equipment work with work of other trades, for proper time and sequence to avoid construction delays.

B.	Install window washing equipment plumb and level in accordance with manufacturer’s written instructions.

C.	[Mechanically fasten anchors in accordance with manufacturer’s recommendations] [Install anchors in concrete in accordance with Section 03 30 00 - Cast-in-Place Concrete and with manufacturer’s recommendations.

D.	Accurately fit and align, securely fasten and install free from distortion or defects.

E.	Deform threads of tail end of anchor studs after nuts have been tightened to prevent accidental removal and vandalism.

3.06	FIELD QUALITY CONTROL

A.	When necessary have the manufacture assist in installation.

B.	Manufacturer’s Field Services: Have manufacturer’s technical representative schedule site visits to review work as follows:

1.	After delivery and storage of products.

2.	When preparatory work for which work of this Section depends is complete, but before installation begins.

3.	[Weekly] [2 times] during progress of work [at [25%] and [60%]] of completion.

4. 	Upon completion of work, after cleaning is carried out.

C.	Testing: Test on site 100% of anchors relying upon chemical adhesive fasteners using load cell test apparatus in accordance with manufacturer's written recommendations.

3.07	ADJUSTMENT

A.	Lubricate moving parts to operate smoothly and fit accurately.

B.	Complete "Initial Inspection - Certification for Use" form included in Equipment Manual and Inspection Log Book provided by manufacturer.

3.08	FINAL CLEANING

A.	Do cleanup in accordance with Section [01 74 00 - Cleaning and Waste Management].

B.	Upon completion, remove surplus and excess materials, rubbish, tools and equipment.

3.09	PROTECTION

A.	Protect installed product from damage during construction in accordance with Section [01 76 00 - Protecting Installed Construction].

B.	Make good damage to adjacent materials caused by window washing equipment installation.

3.10	MAINTENANCE

A.	Include complete maintenance on window washing equipment for [12] months after date of acceptance by [Owner] [Architect] [Consultant].

B.	Repair or replace parts of window washing equipment whenever required due to defect and normal wear and tear.

C.	Use only standard parts of product line of manufacturer of window washing equipment.

D.	Maintain locally adequate stock of parts for replacement or emergency purposes.

E.	Provide personnel to perform work under supervision and in direct employ of window washing equipment system manufacturer or manufacturer's licensed agent.

F.	Perform work during regular trade working hours satisfactory to [Owner] [Architect] [Consultant].

G.	Provide emergency call-back at no extra cost and ensure fulfillment of maintenance and emergency service without undue loss of time to [Owner] [Architect] [Consultant].

H.	Ensure that maintenance personnel register with designated building personnel at time of inspections and maintenance.

END OF SECTION